Compressed Air: Centrifugal Calculations

Control Type: Modulation w/Unload

Figure 1: Mindmap of Process

Variables/Inputs

| Field Name | Name in Math | Units | Imperial Units | Metric Units |
| --- | --- | --- | --- | --- |
| Compressor Rated capacity (aka full load) | C_fl | acfm | acfm |  |
| Power at Full Load Operating Pressure | kW_fl | kW |  | kW |
| Power calculated | kW_calc | kW |  | kW |
| Percent of Full Load Power | PerkW | % (fraction) | - | - |
| Percent Power at Full Load | kWPer_fl | % (fraction) | - | - |
| Percent Power at No Load | kWPer_nl | % (fraction) | - | - |
| Percent Capacity at Full Load | CPer_fl | % (fraction) | - | - |
| Percent Capacity at No Load | CPer_nl | % (fraction) | - | - |
| Percent of Capacity | CPer | % (fraction) | - | - |
| Percent Max Capacity at unload | CPer_ulB | acfm | acfm |  |
| Measured Capacity | C_measured | acfm | acfm |  |
| Surge (blowoff point) Flow | C_blow | acfm | acfm |  |
| Power at (surge) blowoff point | kW_blow | kW |  | kW |
| Percent capacity at blowoff | CPer_blow | % (fraction) | - | - |
| Percent Power at blowoff | kWPer_blow | % (fraction) | - | - |
| Percent Power at unload | kWPer_ul | % (fraction) | - | - |
| Percent Capacity at unload | CPer_ul | % (fraction) | - | - |
| Power at Max full flow (not full load) | kW_max | kW |  |  |
| Capacity at Max full flow (not full load) | C_max | acfm | acfm |  |
| Percent Power at Max full flow (not full load) | kWPer_max | % (fraction) | - | - |
| Percent Capacity at Max full flow (not full load) | CPer_max | % (fraction) | - | - |
| Surge airflow @ design conditions | C_blow | acfm | acfm |  |
| Max Full load (surge) pressure | P_max_surge | psig | psig |  |
| Capacity @max full load pressure | C_max_psi | acfm | acfm |  |
| Min Full Load (stonewall) pressure | P_min | psig | psig |  |
| Capacity @ min full load pressure | C_min_psi | acfm | acfm |  |
| Measured Amps | I_measured | amps | - | - |
| Power Factor | PF | % (fraction) | - | - |
| Measured Voltage | V_measured | V | - | - |

Field Validation

| Field Name | Name in Math | Min | Max | Y/R |
| --- | --- | --- | --- | --- |
| Compressor Rated capacity (aka full load) | C_fl | 0 | N/A | - |
| Power at Full Load Operating Pressure | kW_fl | 0 | N/A | - |
| Power calculated | kW_calc | 0 | kW_calc =< kW_fl | R |
| Percent of Full Load Power | PerkW | 0 | 100 | R |
| Percent Power at Full Load | kWPer_fl | 0 | 100 | R |
| Percent Power at No Load | kWPer_nl | 0 | kWPer_nl <100 | R |
| Percent Capacity at Full Load | CPer_fl | 0 | 100 | R |
| Percent Capacity at No Load | CPer_nl | 0 | 100 | R |
| Percent of Measured Capacity | CPer | 0 | 100 | R |
| Percent Max Capacity at unload | CPer_ulB | 0 | CPer_ul< CPer_ulB<CPer_max | R |
| Measured Capacity | C_measured | 0 | C_measured =< C_fl | R |
| Surge (blowoff point) Flow | C_blow | 0 | C_blow =< C_fl | R |
| Power at (surge) blowoff point | kW_blow | 0 | 100 | R |
| Percent capacity at blowoff | CPer_blow | 0 | 100 | R |
| Percent Power at blowoff | kWPer_blow | 0 | 100 | R |
| Percent Power at unload | kWPer_ul | 0 | 100 | R |
| Percent Capacity at unload | CPer_ul | 0 | 100 | R |
| Power at Max full flow (not full load) | kW_max | 0 | 100 | R |
| Capacity at Max full flow (not full load) | C_max | 0 | C_max =< C_fl | R |
| Percent Power at Max full flow (not full load) | kWPer_max | 0 | 100 | R |
| Percent Capacity at Max full flow (not full load) | CPer_max | 0 | 100 | R |
| Surge airflow @ design conditions | C_blow | 0 | C_blow =< C_fl | R |
| Max Full load (surge) pressure | P_max_surge | 0 | P_max_surge > P_min | R |
| Capacity @max full load pressure | C_max_psi | 0 | C_max_psi =< C_fl | R |
| Min Full Load (stonewall) pressure | P_min | 0 | 100 | R |
| Capacity @ min full load pressure | C_min_psi | 0 | N/A | - |
| Measured Amps | I_measured | 0 | N/A | - |
| Power Factor | PF | 0 | 100 | R |
| Measured Voltage | V_measured | 0 | N/A | - |

Math

Changing Discharge Pressure

When the discharge pressures change the acfm ratings will also change. The user will provide (or default that can be changed) three points. An equation will need to be created based on these three points. See pump/fan curves in measur for calculation “CurveFitVal”.

https://github.com/ORNL-AMO/AMO-Tools-Suite/blob/develop/src/calculator/util/CurveFitVal.cpp

Three points:

(C_min_psi , P_min) , (C_max_psi , P_max_surge) , (C_fl , P_fl)

Below are the values that can be changed using the derived equation. The user can change the pressure and the capacity will need to update accordingly.

| Discharge Pressure (Input) | Airflow (Output) |
| --- | --- |
| P_fl | C_fl |
| P_max | C_max |

Transform User Profile Input:

The user will have to provide a “usage profile.” The usage profile will require data for each hour in a 24-hour period. The user will choose one of five input options. The mindmap at the beginning will show what inputs will have to be transformed. Please not only controls with blow-off will require blowPer as an input and C_blow as an output. The provided data:

| User Inputs | How to Transform | Follow Algorithm for |
| --- | --- | --- |
| C_measured | PerC = C_measured/ C_fl | PerkW |
| V_measured, I_measured, PF, (and blowPer) | kW_measured = V_measured * I_measured * PF * 1.732 / 1000 PerkW = kW_measured / kW_fl | PerC |
| kW_measured (and blowPer) | PerkW = kW_measured / kW_fl | PerC |
| PerC | Continue to algorithm | PerkW |
| PerkW (and blowPer) | Continue to algorithm | PerC |

Profile analysis:

General Equations used regardless of control type, needed for following calculations:

kWPer_nl = kW_nl / kW_fl

CPer_nl = C_nl / C_fl

kWPer_blow = kW_blow / kW_fl

CPer_blow = C_blow / C_fl

kWPer_max = kW_max / kW_fl

CPer_max = C_max / C_fl

CPer_ul = C_ul / C_fl

CPer_ulB = C_ul / C_max

Example:

| Inputs |  | Outputs |  |
| --- | --- | --- | --- |
| Variable | Value | Variable | Value |
| kW_nl | 71.3 | kWPer_nl | .16 |
| kW_fl | 452.3 | CPer_nl | 0 |
| C_nl | 0 | kWPer_blow | .82 |
| C_fl | 3138 | CPer_blow | .80 |
| kW_blow | 370.9 | CPer_max | .96 |
| C_blow | 2510 | kWPer_max | 1 |
| kW_max | 452.3 |  |  |
| C_max | 3011 |  |  |

Control Type: Load/unload

Using Percent Capacity as Input:

PerkW = ((1 - kWPer_nl) / (CPer_fl-CPer_nl))*(CPer) + kWPer_nl

kW_calc = PerkW * kW_fl

C_calc = C_fl * CPer

Example:

| Inputs |  | Outputs |  |
| --- | --- | --- | --- |
| Variable | Value | Variable | Value |
| kWPer_nl | .16 | PerkW | .360 |
| CPer_fl | 1 | kW_calc | 162.7 |
| CPer_nl | 0 | C_calc | 753 |
| CPer | .24 |  |  |

Using Percent Power as Input:

CPer = (PerkW - kWPer_nl) * ((CPer_fl-CPer_nl) / (1 - kWPer_nl))

C_calc = C_fl * CPer

kW_calc = PerkW * kW_fl

Example:

| Inputs |  | Outputs |  |
| --- | --- | --- | --- |
| Variable | Value | Variable | Value |
| kWPer_nl | .16 | CPer | .24 |
| CPer_fl | 1 | kW_calc | 162.7 |
| CPer_nl | 0 | C_calc | 753 |
| PerkW | .36 |  |  |

Figure 2: Performance Profile for Load/unload control type

Control Type: Inlet Butterfly with Blowoff or Inlet Guide Vane with Blowoff

Using Percent Capacity as Input:

IF

CPer < CPer_blow

Then

PerkW = kWPer_blow

blowPer =  CPer_blow - CPer

Else

PerkW = ((1- kWPer_blow)/(1- CPer_blow))*( CPer)+1 -((1 - kWPer_blow)/( 1 - CPer_blow))*1)

kW_calc = PerkW * kW_fl

C_calc = C_fl * CPer

C_blow = blowPer * C_fl

Example:

| Inputs |  | Outputs |  |
| --- | --- | --- | --- |
| Variable | Value | Variable | Value |
| CPer | .94 | PerkW | .946 |
| CPer_blow | .80 | kW_calc | 427.9 |
| kWPer_blow | .82 | C_calc | 2950 |
| kW_fl | 452.3 | C_blow | 0 |
| C_fl | 3138 |  |  |

Using Percent Power and blowoffPer as Input:

IF

PerkW <=kWPer_blow

Then

CPer = CPer_blow- blowPer

Else

CPer = ((1-CPer_blow)/(1-kWPer_blow))*( PerkW -1+((1kWPer_blow)/(1-CPer_blow)))

C_calc = C_fl * CPer

kW_calc = PerkW * kW_fl

C_blow = blowPer * C_fl

Example:

| Inputs |  | Outputs |  |
| --- | --- | --- | --- |
| Variable | Value | Variable | Value |
| PerkW | .82 | CPer | .12 |
| CPer_blow | .80 | kW_calc | 370.9 |
| kWPer_blow | .82 | C_calc | 377 |
| kW_fl | 452.3 | C_blow | 2133 |
| C_fl | 3138 |  |  |
| blowPer | .6798 |  |  |

Figure 3: Performance Profile for Blowoff Control Type

Control Type: Inlet Guide Vane Modulation with Unloading or Butterfly Modulation with unloading

Using Percent Capacity as Input:

IF

CPer <kWPer_ul

Then

PerkW = ((kWPer_ul - kWPer_nl)/( CPer_ul - CPer_nl))*( CPer)+ kWPer_nl

Else IF

CPer < CPer_max

Then

PerkW = ((kWPer_max - kWPer_ul)/( CPer_max - CPer_ul))*( CPer)+ kWPer_max -(( kWPer_max - kWPer_ul)/( CPer_max - CPer_ul))* CPer_max

Else

PerkW = 1

kW_calc = PerkW * kW_fl

C_calc = C_fl * CPer

Example:

| Inputs |  | Outputs |  |
| --- | --- | --- | --- |
| Variable | Value | Variable | Value |
| CPer | .24 | PerkW | .367 |
| kWPer_ul | .92 | kW_calc | 165.9 |
| kWPer_nl | .16 | C_calc | 753 |
| CPer_ul | .87 |  |  |
| kWPer_max | 1 |  |  |
| CPer_max | .96 |  |  |
| kW_fl | 452.3 |  |  |
| C_fl | 3138 |  |  |

Using Percent Power as Input:

IF

PerkW <=kWPer_nl

Then

CPer = CPer_nl

Else IF

PerkW < kWPer_ul

Then

CPer  = (PerkW -kWPer_nl)*(( CPer_ul - CPer_nl)/( kWPer_ul -kWPer_nl))

Else IF

PerkW >= kWPer_ul

Then

CPer  = ((1- CPer_ulB)/( kWPer_max - kWPer_ul))* PerkW +(1-(1 - CPer_ulB)/( kWPer_max - kWPer_ul))

Else

CPer  = 1

IF

CPer < CPer_ulB

Then

C_calc = CPer * C_fl

Else

C_calc = CPer * C_max

kW_calc = PerkW * kW_fl

Example:

| Inputs |  | Outputs |  |
| --- | --- | --- | --- |
| Variable | Value | Variable | Value |
| PerkW | .94 | CPer | .933 |
| kWPer_ul | .92 | kW_calc | 425 |
| kWPer_nl | .158 | C_calc | 2809 |
| kWPer_max | 1 |  |  |
| CPer_max | .96 |  |  |
| kW_fl | 452.3 |  |  |
| C_fl | 3138 |  |  |
| CPer_ulB | .91 |  |  |
| C_max | 2731 |  |  |
| CPer_ul | .87 |  |  |

Figure 4: Performance Profile for Modulation with Unload